## Base_Case_Group3
Symbol | Value | Unit | Description | edit values in yellow, not the other ones
Tsource-in | 125 | °C | Temperature of the geothermal fluid from the production wells | Group3: avg production T at t=100yr (FEFLOW result, see breakthrough curve F3)
Tsource-out | 50 | °C | Reinjection temperature (generally 50-80°C, limited by silica scaling risk)
Tcond-in | 14 | °C | Outdoor dry bulb temperature (annual mean, Volterra/Pomarance area, near Larderello)
Tcond-out | 26 | °C | Outlet temperature in the air condenser (generally, 12-15°C higher than Tcond-in)
LMTsource | 86.1965 | °C | Log-mean temperature at source side
LMTair | 19.9591 | °C | Log-mean temperature at condenser side
etaLorentz | 18.43% | - | Gross electrical efficiency of the ORC turbine - maximum theoretical value after Lorentz
etaCarnot | 27.88% | - | Gross electrical efficiency of the ORC turbine - maximum theoretical value after Carnot
etaORC/etaLorentz | 52% |  | % of the Lorentz efficiency achieved by the turbine - net value excluding own consumption
etaORC | 9.585% |  | Net electrical efficiency of the ORC turbine
cP fluid | 4.31 | kJ/kg/K | Specific heat of the geothermal fluid (assume water values if you do not know)
density fluid | 0.917 | kg/l | Density of the geothermal fluid (assume water values if you do not know)
volumetric flow rate | 150 | l/s | Volumetric (l/s) and mass (kg/s) flow rate of the geothermal fluid (Group3: 5 x 30 l/s)
mass flow rate | 137.55 | kg/s
Pth-source | 44463.0375 | kW | Thermal power extracted from the reservoir
Pel | 4261.795 | kW | Electrical power of the ORC turbine
LF | 8000 | h/a | Load factor of the ORC turbine
Prod-el-year | 34094.3603 | MWh/a | Electrical production per year
days of the month | 31
Prod-el-month | 3170.7755 | MWh/month | Electrical production per month

## Monthly_Production
Monthly electrical production — Group 3 (source: Base_Case_Group3 sheet, Tsource fixed)
Outdoor temperature source: Volterra / Pomarance climate normals (near Larderello), climate-data.org, 1991-2021 avg.
Availability factor (from Base_Case LF / 8760 h) | [6 empty] | 0.91324
Month | Days | T_outdoor avg [°C] | Tcond-out [°C] | LMTair [°C] | eta_Lorentz [-] | eta_ORC [-] | Pel [kW] | Prod-el-month [MWh]
January | 31 | 5 | 17 | 10.9578 | 0.20938 | 0.10888 | 4840.9492 | 3289.1928
February | 28 | 5.7 | 17.7 | 11.6579 | 0.20743 | 0.10786 | 4795.9036 | 2943.2395
March | 31 | 9 | 21 | 14.9584 | 0.19824 | 0.10309 | 4583.5467 | 3114.3002
April | 30 | 12.5 | 24.5 | 18.4589 | 0.1885 | 0.098021 | 4358.3204 | 2865.7449
May | 31 | 16.5 | 28.5 | 22.4594 | 0.17737 | 0.092232 | 4100.9198 | 2786.3784
June | 30 | 21 | 33 | 26.96 | 0.16485 | 0.085719 | 3811.3453 | 2506.0901
July | 31 | 23.7 | 35.7 | 29.6604 | 0.15733 | 0.081812 | 3637.6011 | 2471.5756
August | 31 | 23.7 | 35.7 | 29.6604 | 0.15733 | 0.081812 | 3637.6011 | 2471.5756
September | 30 | 19.2 | 31.2 | 25.1598 | 0.16985 | 0.088324 | 3927.1749 | 2582.252
October | 31 | 15 | 27 | 20.9592 | 0.18154 | 0.094403 | 4197.4449 | 2851.9626
November | 30 | 10.2 | 22.2 | 16.1585 | 0.1949 | 0.10135 | 4506.3261 | 2963.0638
December | 31 | 6.1 | 18.1 | 12.0579 | 0.20631 | 0.10728 | 4770.1634 | 3241.0973
Notes: | [7 empty] | 34086.4727
- Tsource-in, Tsource-out, cP, density, flow rate taken from Base_Case_Group3 sheet (fixed, do not vary seasonally in this model).
- Availability factor applies the same total operating hours (LF, cell B18 in Base_Case) as the annual estimate, distributed pro-rata by days/month.
- Yellow cells (T_outdoor avg) are editable; replace with your own monthly climate data source if desired.